Annex II Technical Specifications

STRUCTURED CABLING WORKS AT FIELD OFFICES: GORI, ZUGDIDI AND MTSKHETA OF THE EUMM GEORGIA

1. OBJECTIVE, PURPOSE & EXPECTED RESULTS

1.1 Overall objective

The overall objective of the project of which this contract will be a part is as follows:

To implement a star-wired reliable CAT5e (or higher) structured cabling infrastructure fully compliant with the best practices of installation including the quality of civil works and international standards EIA/TIA 568-B, IS11801 and EN50173, in order to efficiently streamlining and distributing a variety of data/voice services throughout the location, ensuring flexibility, fault tolerance and minimal maintenance, in the following locations and order:

LOT 2

Location 3: Field Office Mtskheta

Mtskheta

9 David Agmanshenebeli Lane

1.2 Purpose

The purpose of implementing the structured cabling system (SCS) in the locations is to increase the appropriate level of consistency and life-cycle of the installations offering support for multi-vendor equipment, simplifying the moves/adds/changes of the equipment, simplifying troubleshooting and supporting future applications and services.

1.3 Results to be achieved by the Contractor

- The Specialist Contractor shall provide a detailed Comm’s Design Package submittal to EUMM for approval prior to commencing the works on site. The Design package shall include the routes of the cable conduits, the estimated quantities and type of materials to be used, the civil works to be done (holes, etc.)

- The Specialist Contractor shall implement a fully CAT5e (or higher) certified communications wiring infrastructure in accordance with the project description:

- Field Office Mtskheta:  104 * CAT5e (or higher) UTP Data Outlets/cable runs, as shown in the drawings (Annex III) presented on a RJ45 socket mounted in PVC/plastic dado trunking.

- Provide for the voice/data outlets and subsystems/components as indicated in the project description. The Specialist Contractor shall note that EUMM shall install, test and commission: computer and wireless active equipment and hardware, servers and network active equipment.

- Provide test results and certifications attesting fully compliance with the electrical and physical specifications of CAT5e (or higher) performance standards.

2. ASSUMPTIONS & RISKS

2.1 Assumptions underlying the project intervention

N\A

2.2 Risks

Usual risk as observed in the post conflict environment and geographic position of Georgia.

Clearance for the civil works not provided by the building owner, ante or during the contract execution.

3. SCOPE OF THE WORK

3.1 Project description

3.1.1 Specific Requirements – Key notes

- All products shall comply with CAT5e (or higher) standard, EIA/TIA 568-B, IS 11801, EN 50173;

- Class D channel performance of 100 MHz is required;

- The Contractor shall comply fully to these specifications.

3.1.2 Scope of work

3.1.2.1 INSTALLATION

- Supply, deliver, install, test and commission a registered CAT5e (or higher) solution to comply with EIA/TIA 568-B, IS11801 and EN50173 in each location;

- Supply and install all associated equipment specified or required for the successful completion of the above;

3.1.2.2 GENERAL

- All work shall be done in a thorough and conscientious manner according to industry guidelines and standards, and shall be subject to inspection and acceptance.

- The contractor shall be certain that all installation work areas are secured and made safe in accordance with Health and Safety regulations.

- An appropriate construction schedule shall be delivered by the Contractor and will be subject to approval by the Contracting Authority. The construction schedule is expected to encompass a number of months for all three field offices and should include at least one installation supervisor or lead technician, for on-site management of the project;

- The contractor shall be responsible for completing a detailed informative note addressing the weekly progress of the installation schedule and send it to the EUMM Project manager;

- The contractor shall maintain a work area free of debris, rubbish, empty cable reels, scrap wire, etc., and dispose of such items on a daily basis;

- The contractor shall take precautions to avoid damage to the premises and property. Should any damage occur, the contractor will perform any restoration / redecoration works needed to restore the property to the conditions it was prior of commencing the works;

- The contractor shall provide any necessary screws, anchors, clamps, tie wraps, distribution rings, miscellaneous grounding and support hardware, etc., necessary to facilitate the installation of the distribution system;

- The contractor shall be responsible for labelling all cables and cords, distribution frames and outlet locations, according to industry standards.  Labels should be computer generated or typewritten;

- It shall be the responsibility of the installation contractor to furnish any special installation equipment or tools necessary to properly complete the installation.  This may include tools for terminating cables, testing and splicing equipment for copper/fibre cables, communication devices, jack stands for cable reels, or cable winches;

- The contractor shall not place any distribution cabling alongside power lines, or share the same conduit, channel or sleeve with electrical apparatus without appropriate separation as defined by the relevant European / international standards;

- The contractor shall ensure that the maximum pulling tensions of the specified distribution cables are not exceeded at any time during the placement of the facilities.  Failure to follow the appropriate guidelines may require the contractor to provide the additional material and labour necessary to properly rectify the situation;

- This shall also apply to any and all damages sustained to the cables by the installation contractor during the implementation;

- The contractor shall be responsible for providing an approved ground at all newly installed distribution frames and protector locations insuring proper bonding to existing facilities. The contractor shall also be responsible for ensuring ground continuity by properly bonding all appropriate cabling, closures, cabinets, service boxes and framework.  All grounds shall consist of appropriate gauge copper wire and shall be supplied from an approved building ground and bonded to the main electrical ground.

    - The contractor shall have appropriate Employers Liability Public Liability insurance.

    - The contractor shall be required to produce evidence from the manufacturer, that he is certified to install the specified product.

3.1.2.3  SYSTEM REQUIREMENTS

The system offered and quoted, shall incorporate all features and facilities listed in this specification.

3.1.2.3.1 Specifications

The solution shall consist of any or all of the following subsystems:

- Work location subsystem

- Cabling (star-wired) subsystem

- Administration subsystem

The systems shall:

- Support analogue and digital applications, data, local area networks (LAN) on a common cabling platform.

The systems that shall be supported include, but are not limited to:

- Data Communications – Applications standards supported should include, but not limited to, IEEE 802.3 10BASE-T, IEEE 802.3 100Base-T and 1000BASE-T. In addition, cables shall be capable of supporting current and evolving high-speed, high-bandwidth applications.

- Voice Applications – Analogue and digital voice.

- Cover its capacity and functionality with minimum components;

- Be flexible and capable of including new facilities or technologies as they become required or available;

- The system shall specifically support the applications and associated transmission distances described in the industry standards;

- The cabling installation shall comply with ISO IS14763, EN50174 and TIA/EIA 569. It shall also comply with the channel performance of the proposed new editions of TIA/EIA 568-B, IS 11801 and EN50173 standards (or the standard itself if ratified before installation commences).

3.1.2.3.2 System Channel Performance

The solutions must focus on the performance of the channel as a whole, rather than the performance of individual components. This is a more useful parameter for measuring performance as it takes into account the combined components required to move a signal from the closet to the desktop, thus providing a guarantee for the total signal quality.

The system as a whole should meet or exceed the following guaranteed channel performance values:

| Frequency (MHZ) | 1 | 4 | 10 | 20 | 31.25 | 62.5 | 100 | 155 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Insertion Loss (dB/100m) | 2.2 | 4.5 | 7.1 | 10.2 | 12.9 | 18.6 | 24.0 | -- |
| NEXT (dB) | 60.0 | 53.5 | 47.0 | 42.0 | 38.7 | 33.6 | 30.1 | -- |
| PSNEXT (dB) | 57.0 | 50.5 | 44.0 | 39.0 | 35.7 | 30.6 | 27.1 | -- |
| ACRF (dB) | 57.4 | 45.4 | 37.4 | 31.4 | 27.5 | 21.5 | 17.4 | -- |
| PSACRF (dB) | 54.4 | 42.4 | 34.4 | 28.4 | 24.5 | 18.5 | 14.4 | -- |
| RL (dB) | 17.0 | 17.0 | 17.0 | 17.0 | 15.1 | 12.1 | 10.1 | -- |

3.2.2 System Design

3.2.3.1. Work Location Subsystem

- The connection between the information outlet and the station equipment in the work area is provided by the work area subsystem.

- Contractor shall supply the wiring or cords that connect terminal devices to information outlets, same colour (white/grey) and manufacturer. This includes mounting cords and connectors needed:

  - 5m RJ45 - RJ45 Category 5e or better patch leads;

3.2.3.2 Cabling Subsystem

- The CABLING subsystem provides connections in a star topology, from the Administration System (Telecommunication Room) to the work area information outlets (IOs). It consists of transmission media, the associated connected hardware terminating this media and IOs in the working area.

- The Contractor shall provide Voice/Data CAT5e (or higher) RJ-45 outlets on dado trunking;

- The type of the cables used shall be 4-pair unshielded twisted pair (UTP), CAT5e (or higher).

- The cable shall be able to support voice and data up to 1Gbps.

- The 4 pair cables should be at minimum Independently Verified to be Category 5e (or higher) by Underwriters Laboratories (UL).

- The 4-pair UTP cable shall be run using a star topology format from the termination block/rack in the administration subsystem to every individual information outlet. All cable routes to be approved prior to installation of the cabling.

- The length of each individual run of network cable from the administration subsystem Telecommunications Room) to the information outlet shall not exceed 90 metres.

- Contractor shall observe the bending radius and pulling strength requirements, given below, of the 4-pair UTP, cable during handling and installation: Bending radius - 4 times the cable diameter Maximum pulling tension - 11N

  - Bending radius - 4 times the cable diameter

  - Maximum pulling tension - 11N

- Each run of cable between the termination block and the information outlet shall be continuous without any joints.

3.2.3.3 Information Outlets

- The necessary number of Information Outlets and their distribution is indicated in the drawings:

  - Field Office Mtskheta = 104 outlets

Note: the information outlets position/location will be recommended by the Contractor and approved by the EUMM Project Manager.

- Comms outlet plates shall be “MK” Logic Plus (WHI) manufacture assembly or equivalent c/w Krone, Systimax or equivalent CAT5e (or higher) RJ-45 devices. Provide twin back box c/w quad outlet plate at each location. Provide blank outlet covers where required.

- Where vertical mounted dado or power poles are provided Twin face plates shall be used to provide the required quantity of Information Outlets.

- All information outlets shall be of EN 60603-7 (IEC 603-7) and EN 28877 (ISO 8877) 8-position modular MGS400 connectors and of the insulation displacement type. They shall be capable of receiving of 24 AWG solid and stranded wires.

- The information outlet shall be either surface or flush mounted in appropriate face plates or floor boxes.

- The RJ45 information outlet shall be multi-vendor supportive and shall be wired in an EIA/TIA 568-B configuration

- The RJ45 information outlet shall meet or exceed the Category 5e requirements of the ANSI/EIA/TIA 568-B, ISO IS 11801 and EN 50173 standards.

3.2.3.4 Administration Subsystem

The administration subsystem links all of the subsystems together. It consists of labelling hardware for providing circuit identification and patch cords used for creating circuit connections at the cross connects.

The administration subsystem shall consist of RJ45 patch panels for termination of copper cables mounted in a Standard 42U Rack unit as specified in 4.1.3.3.5.

All aspects are to be approved prior to installation by the contracting authority Project Manager.

3.2.3.4.1. Termination Block

The Termination block shall be able to accommodate 24 AWG cable conductors, solid and stranded. The block shall meet or exceed the relevant requirements of ANSI/EIA/TIA 568-B, ISO IS11801 and EN50173 standards.

The Termination blocks shall be Underwriter's Laboratories (UL) listed for guaranteed performance.

The Termination blocks shall be mounted in Standard 42U Racks according the specifics laid down in point 4.1.3.3.5.

3.2.3.4.2. RJ-45 Patch Panels

RJ45 Patch Panels shall be 1U in size and able to accommodate 24 AWG (0.51 mm) stranded and solid cable conductors. The panels shall meet or exceed the ANSI/EIA/TIA 568-B, ISO IS 11801 and EN 50173 Category 5e standards.

In order to provide termination to 150x 4-pair UTP cables, 7 (seven) 24-ports RJ45 patch panels shall be installed.

One cable management unit (2U in size) for each RJ45 patch panel is to be installed, allowing 1U network switches (not to be part of the contract) to be easily placed by the contracting authority between cable management units.

The frame layout is to be approved prior to installation by the contracting authority Project Manager.

Category 5e (or higher) patch leads must be provided for all and each required connection.

3.2.3.3.3. Cable Identification and Labeling

- The contractor shall install a labelling system allowing quick and unique identification of each UTP cable at both terminations (information outlets and patch panels). All details are to be approved prior to installation by the contracting authority Project Manager.

- All labelling shall confirm to the agreed labelling and identification standards.

3.2.3.3.4. Port Plans

- The  Contractor shall include for maintaining an accurate detailed record of the Works as they progress.  The Specialist IT structured wiring contractor shall include for supplying copies of ‘As-Installed’ Port Plans upon completion of each area.  Drawings shall be in CAD form and shall be submitted to the Project Manager as directed.

3.2.3.3.5. Rack unit

- The contractor shall supply one (1) x 42U Standard 19“ Rack unit, 800x1000 mm with vertical steel and lockable doors and install it in the Telecommunication Room.

- All Termination blocks, RJ45 patch panels, and cable management units shall be installed in the specified Rack unit.

- The Rack unit  shall include 2 x vertically mounted type Power Distribution Units (PDUs) min 8 sockets each, to power standard server/telecom equipment.

- The Contractor shall make the necessary electrical connections from the building electrical system as indicated by the Project Coordinator to the vertically mounted type PDUs. A minimum 16A circuit shall be installed from existing UPS to the rack as directed by contracting authority Project Manager.

- HANDOVER AND SITE REGISTRATION

  - Punchdown, Testing and Commissioning

- The Contractor shall be responsible for punch down at each end of each Voice/Data Cable, together with testing and commissioning to current requirements and for Warranty purposes.  All cables shall be 100% TDR tested with results recorded on disc.

- All circuits shall be tested with a Fluke DTX, LanTEK II analysers or equivalent cable certification tester and all results shall be recorded at the client.

- The specialist IT structured wiring contractor shall provide two hard copies and two soft copies (CD/DVD) of Operating and maintenance manuals consisting generally of As-Installed Drawings, Hardware Manuals, Test Sheets, Port Plans, Certification and Warranty.

- The installation shall be fully tested (i.e. 100% of all cables) to comply with ISO/TEC 11801, TIA/EIA 568B to CAT5e (or higher) limits.

- Level III test instruments shall be used and all test results recorded on disc and included in the hand-over documents.

- Cables that fail the test must be replaced.  Contracting Authority reserves the right to witness some or all of the testing.

- The specialist contractor shall include for detailed hand-over documentation to include:

- Product Warranty – 2 Copies

- Test results on CD  – 2 Copies

- As-Installed drawings on CD  – 2 Copies

    - General

The Contractor shall include for fishing cables through conduits and trunking throughout.

The contractor will be responsible for the installation of all containment i.e. tray / conduit and any associated civil works, as well as making good after.  All containment should be filled to a maximum of 60%, thus leaving a 40% margin for additional cables.

    - Patch Cords

The system shall be completed with high grade Patch Cords and Connectors to Category 5e or higher.

Patch cords shall support Data Speeds up to 1000Mb/Sec.

The specialist IT structured wiring contractor shall include for Patch Cords and device cables as detailed in the specific scope of work;

    - Co-ordination of Services

The Contractor shall include for co-ordinating the work as described herein and shall have regard for all other works in progress during the installation of the IT structured wiring system.

The specialist contractor shall not put in hand any work under this section without Written Approval of the Project Manager.

    - Warranty:

The entire cabling infrastructure shall be fully guaranteed for a minimum period of 2 (two) years. The Specialist Contractor shall be required to produce Warranties and Guarantees in this regard.

The warranty must be complete, unambiguous and give the Contracting Authority the appropriate assurances.

The provision of manufacturer’s warranty on the entire cabling infrastructure is highly desirable..

Warranties shall include for the following:

- Compliance with TIA/EIA 568-B, IS 11801 and EN 50173 standards (with no get out clauses)

- Independent UL tested system, no other lab is acceptable;

- Products and labour for replacement of products (in the event of a problem) the products must be manufactured by a single manufacturer;

- The warranty must cover full ‘channel’ and not just the ‘permanent link;

- The warranty must be issued by a manufacturer and not a contractor or a distributor;

- The warranty must provide full application assurance;

- PROJECT ADMINISTRATION

EUMM will designate a Project Coordinator which shall be responsible for the coordination of activities under the Contract.

During the course of their work under this Contract, including field work, the Contractor may be required to complete timesheets or any other document used to identify time spent, as instructed by the Project Coordinator.

- PERFORMANCE

The Consultant undertakes to perform the Services with the highest standards of professional and ethical competence and integrity.

- CONFIDENTIALITY

The Consultant shall not, during the term of this Contract and within three years after its expiration, disclose any proprietary or confidential information relating to the Services, this Contract or the Contracting Authority’s business or operations without the prior written consent of the Contracting Authority.

Any violation of the secrecy obligation during the course of the present contract may be considered by the Contracting Authority as a cause justifying immediate termination of the present contract without notice and without prejudice to the right of the Contracting Authority to claim damages.

- OWNERSHIP OF THE MATERIAL

Any studies, reports, drawings, specifications instruction manuals, daily reports, minutes or meetings, oral or written data, or other material, graphic, software or otherwise, prepared by the Consultant for the Contracting Authority under the Contract shall belong to and remain the property of the Contracting Authority.